## 4P 3PH rating
Dingol Generator Rating Table (4-pole 3-phase rating)
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  |  |  | 110-120 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 13 |  | 14 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | 8.1 | 6.5 | 8.1 | 6.5 | 8.1 | 6.5 | 6.2 | 4.96 | - | - | 9.6 | 7.7 | 9.6 | 7.7 | 10.2 | 8.2 | 10.2 | 8.2 | 10.2 | 8.2
DG164B | 11 | 8.8 | 11 | 8.8 | 11 | 8.8 | 8.4 | 6.72 | - | - | 13 | 10.4 | 13 | 10.4 | 13.8 | 11 | 13.8 | 11 | 13.8 | 11
DG164C | 13.5 | 10.8 | 13.5 | 10.8 | 13.5 | 10.8 | 11 | 8.8 | - | - | 16 | 12.8 | 16 | 12.8 | 16.9 | 13.5 | 16.9 | 13.5 | 16.9 | 13.5
DG164D | 16 | 12.8 | 16 | 12.8 | 16 | 12.8 | 13.5 | 10.8 | - | - | 20 | 16 | 18.9 | 15.1 | 20 | 16 | 20 | 16 | 20 | 16
DG184ES | 20 | 16 | 20 | 16 | 20 | 16 | 15 | 12 | - | - | 25 | 20 | 24 | 19.2 | 25 | 20 | 25 | 20 | 25 | 20
DG184E | 22.5 | 18 | 22.5 | 18 | 22.5 | 18 | 17.5 | 14 | - | - | 27.5 | 22 | 27.5 | 22 | 28.8 | 23 | 28.8 | 23 | 30 | 24
DG184F | 27.5 | 22 | 27.5 | 22 | 27.5 | 22 | 22 | 17.6 | - | - | 32.5 | 26 | 32.5 | 26 | 34.4 | 27.5 | 34.4 | 27.5 | 35 | 28
DG184G | 31.3 | 25 | 31.3 | 25 | 31.3 | 25 | 25 | 20 | - | - | 37.5 | 30 | 35 | 28 | 37.5 | 30 | 37.5 | 30 | 37.5 | 30
DG184H | 37.5 | 30 | 37.5 | 30 | 37.5 | 30 | 30 | 24 | - | - | 43.5 | 34.8 | 44.3 | 35.4 | 46.9 | 37.5 | 46.9 | 37.5 | 46.9 | 37.5
DG184J | 40 | 32 | 40 | 32 | 40 | 32 | 32 | 25.6 | - | - | 47.5 | 38 | 47.3 | 37.84 | 50 | 40 | 50 | 40 | 50 | 40
DG224C | 42.5 | 34 | 42.5 | 34 | 42.5 | 34 | 30 | 24 | - | - | 55 | 44 | 50 | 40 | 52.5 | 42 | 52.5 | 42 | 55 | 44
DG224D | 50 | 40 | 50 | 40 | 50 | 40 | 37.5 | 30 | - | - | 62.5 | 50 | 60 | 48 | 62.5 | 50 | 62.5 | 50 | 65 | 52
DG224E | 60 | 48 | 60 | 48 | 60 | 48 | 45 | 36 | - | - | 70 | 56 | 67.5 | 54 | 70 | 56 | 70 | 56 | 75 | 60
DG224F | 72.5 | 58 | 72.5 | 58 | 72.5 | 58 | 55 | 44 | - | - | 85 | 68 | 83.8 | 67 | 87.5 | 70 | 87.5 | 70 | 93.8 | 75.04
DG224G | 85 | 68 | 85 | 68 | 85 | 68 | 75 | 60 | - | - | 100 | 80 | 93.8 | 75 | 97.5 | 78 | 100 | 80 | 103.8 | 83.04
DG274C | 100 | 80 | 100 | 80 | 100 | 80 | - | - | - | - | 120 | 96 | 112.5 | 90 | 117.5 | 94 | 117.5 | 94 | 125 | 100
DG274D | 125 | 100 | 125 | 100 | 125 | 100 | - | - | - | - | 140 | 112 | 140 | 112 | 150 | 120 | 150 | 120 | 150 | 120
DG274E | 140 | 112 | 140 | 112 | 140 | 112 | - | - | - | - | 160 | 128 | 160 | 128 | 168 | 134 | 168 | 134 | 178 | 142.4
DG274EL | 150 | 120 | 150 | 120 | 150 | 120 | - | - | - | - | 170 | 136 | 170 | 136 | 180 | 144 | 180 | 144 | 190 | 152
DG274F | 160 | 128 | 160 | 128 | 160 | 128 | - | - | - | - | 180 | 144 | 181 | 144.8 | 190 | 152 | 190 | 152 | 200 | 160
DG274G | 180 | 144 | 180 | 144 | 180 | 144 | - | - | - | - | 200 | 160 | 200 | 160 | 213 | 170.4 | 213 | 170.4 | 220 | 176
DG274H | 200 | 160 | 200 | 160 | 200 | 160 | - | - | - | - | 237.5 | 190 | 237 | 189.6 | 245 | 196 | 245 | 196 | 250 | 200
DG274J | 225 | 180 | 225 | 180 | 225 | 180 | - | - | - | - | 280 | 225 | 269 | 215.2 | 281 | 225 | 281 | 224.8 | 300 | 240
DG274K | 250 | 200 | 250 | 200 | 250 | 200 | - | - | - | - | 300 | 240 | 291 | 232.8 | 300 | 240 | 300 | 240 | 312.5 | 250
DG444C | 250 | 200 | 250 | 200 | 250 | 200 | 250 | 200 | 300 | 240 | 300 | 240 | 287.5 | 230 | 300 | 240 | 300 | 240 | 312.5 | 250
DG444D | 300 | 240 | 300 | 240 | 300 | 240 | 280 | 224 | 350 | 280 | 350 | 280 | 340 | 272 | 360 | 288 | 360 | 288 | 375 | 300
DGK444D | 313 | 250 | 313 | 250 | 313 | 250 | 290 | 232 | 360 | 288 | 360 | 288 | 350 | 280 | 375 | 300 | 375 | 300 | 388 | 310.4
DG444E | 325 | 260 | 325 | 260 | 325 | 260 | 325 | 260 | - | - | - | - | 381 | 304.8 | 400 | 320 | 400 | 320 | 415 | 332
DGK444E | 350 | 280 | 350 | 280 | 350 | 280 | 350 | 280 | - | - | - | - | 400 | 320 | 420 | 336 | 420 | 336 | 430 | 344
DG444F | 375 | 300 | 375 | 300 | 375 | 300 | 375 | 300 | 475 | 380 | - | - | 444 | 355.2 | 455 | 364 | 463 | 370.4 | 475 | 380
DGK444F | 400 | 320 | 400 | 320 | 400 | 320 | 400 | 320 | 500 | 400 | - | - | 454 | 363.2 | 480 | 384 | 500 | 400 | 500 | 400
DG544C | 450 | 360 | 450 | 360 | 450 | 360 | 450 | 360 | 500 | 400 | 500 | 400 | 525 | 420 | 550 | 440 | 581 | 464.8 | 594 | 475.2
DG544D | 500 | 400 | 500 | 400 | 500 | 400 | 500 | 400 | 625 | 500 | 625 | 500 | 575 | 460 | 594 | 475.2 | 625 | 500 | 644 | 515.2
DG544ES | 563 | 450.4 | 563 | 450 | 563 | 450 | 563 | 450.4 | 650 | 520 | 650 | 520 | 625 | 500 | 650 | 520 | 670 | 536 | 700 | 560
DG544E | 600 | 480 | 600 | 480 | 600 | 480 | 600 | 480 | 687.5 | 550 | 688 | 550.4 | 681 | 544.8 | 713 | 570.4 | 732 | 585.6 | 750 | 600
DG544EL | 625 | 500 | 625 | 500 | 625 | 500 | 625 | 500 | 710 | 568 | 710 | 568 | 700 | 560 | 735 | 588 | 755 | 604 | 765 | 612
DG544F | 670 | 536 | 670 | 536 | 670 | 536 | 650 | 520 | 800 | 640 | 800 | 640 | 738 | 590.4 | 775 | 620 | 800 | 640 | 825 | 660
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 13 |  | 14 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG634B | 710 | 568 | 750 | 600 | 750 | 600 | 680 | 544 | 938 | 750 | 938 | 750 | 810 | 648 | 855 | 684 | 895 | 716 | 938 | 750.4
DG634C1 | 760 | 608 | 800 | 640 | 800 | 640 | 725 | 580 | - | - | - | - | 865 | 692 | 916 | 732.8 | 958 | 766.4 | 1000 | 800
DG634D | 865 | 692 | 910 | 728 | 910 | 728 | 825 | 660 | 1063 | 850 | 1063 | 850 | 986 | 788.8 | 1034 | 827.2 | 1090 | 872 | 1138 | 910.4
DG634E | 950 | 760 | 1000 | 800 | 1000 | 800 | 910 | 728 | 1250 | 1000 | 1250 | 1000 | 1083 | 866.4 | 1145 | 916 | 1197 | 957.6 | 1250 | 1000
DG634F | 1090 | 872 | 1130 | 904 | 1130 | 904 | 1025 | 820 | 1320 | 1056 | 1320 | 1056 | 1204 | 963.2 | 1274 | 1019.2 | 1332 | 1065.6 | 1390 | 1112
DG634G | 1190 | 952 | 1250 | 1000 | 1250 | 1000 | 1135 | 908 | 1500 | 1200 | - | - | 1310 | 1048 | 1386 | 1108.8 | 1449 | 1159.2 | 1513 | 1210.4
DG734B | 1360 | 1088 | 1400 | 1120 | 1400 | 1120 | 1375 | 1100 | 1560 | 1248 | - | - | 1525 | 1220 | 1625 | 1300 | 1655 | 1324 | 1690 | 1352
DG734C | 1505 | 1204 | 1550 | 1240 | 1550 | 1240 | 1520 | 1216 | 1770 | 1416 | - | - | 1705 | 1364 | 1815 | 1452 | 1855 | 1484 | 1890 | 1512
DG734D | 1615 | 1292 | 1650 | 1320 | 1650 | 1320 | 1620 | 1296 | 1915 | 1532 | - | - | 1815 | 1452 | 1935 | 1548 | 1975 | 1580 | 2015 | 1612
DG734E | 1845 | 1476 | 1900 | 1520 | 1900 | 1520 | 1865 | 1492 | - | - | - | - | 2070 | 1656 | 2210 | 1768 | 2250 | 1800 | 2300 | 1840
DG734F | 2020 | 1616 | 2080 | 1664 | 2080 | 1664 | 2040 | 1632 | 2500 | 2000 | - | - | 2345 | 1876 | 2500 | 2000 | 2550 | 2040 | 2600 | 2080
DG734G | 2135 | 1708 | 2200 | 1760 | 2200 | 1760 | 2160 | 1728 | - | - | - | - | 2420 | 1936 | 2535 | 2028 | 2625 | 2100 | 2750 | 2200
DG734H | 2270 | 1816 | 2340 | 1872 | 2340 | 1872 | 2300 | 1840 | - | - | - | - | 2525 | 2020 | 2640 | 2112 | 2725 | 2180 | 2830 | 2264
Notes：
1. DG634C has no W11 option
2. DGK-foluted fan
3. The above rating is based on 40 degree C ambient and 125K temperature rising below 1000 meters altitude above sea.
4. DG734B～H has only W12 option

## 4P 1PH rating
Dingol Generator Rating Table (4-pole 1-phase rating)
Model | Single Phase 50Hz 1500RPM | [11 empty] | Single Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 1 |  | 1 |  | 1 |  | 0.8 |  | 0.8 |  | 0.8 |  | 1 |  | 1 |  | 1
Volts
Series | 220 |  | 230 |  | 240 |  | 220 |  | 230 |  | 240 |  | 220 |  | 230 |  | 240 |  | 220 |  | 230 |  | 240
Parallel | 110 |  | 115 |  | 120 |  | 110 |  | 115 |  | 120 |  | 110 |  | 115 |  | 120 |  | 110 |  | 115 |  | 120
Winding No. | 05 |  | 05 |  | 05 |  | 05 |  | 05 |  | 05 |  | 06 |  | 06 |  | 06 |  | 06 |  | 06 |  | 06
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | 5.4 | 4.3 | 5.4 | 4.3 | 5.4 | 4.3 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.4 | 5.1 | 6.4 | 5.1 | 6.4 | 5.1 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
DG164B | 7.4 | 5.9 | 7.4 | 5.9 | 7.4 | 5.9 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.8 | 7 | 8.8 | 7 | 8.8 | 7 | 11 | 11 | 11 | 11 | 11 | 11
DG164C | 9 | 7.2 | 9 | 7.2 | 9 | 7.2 | 11 | 11 | 11 | 11 | 11 | 11 | 10.8 | 8.6 | 10.8 | 8.6 | 10.8 | 8.6 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
DG164D | 10.8 | 8.6 | 10.8 | 8.6 | 10.8 | 8.6 | 13 | 13 | 13 | 13 | 13 | 13 | 13.5 | 10.8 | 13.5 | 10.8 | 13.5 | 10.8 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
DG184ES | 12.5 | 10 | 12.5 | 10 | 12.5 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 12 | 15 | 12 | 15 | 12 | 18 | 18 | 18 | 18 | 18 | 18
DG184E | 15 | 12 | 15 | 12 | 15 | 12 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 18.4 | 14.7 | 18.4 | 14.7 | 18.4 | 14.7 | 21 | 21 | 21 | 21 | 21 | 21
DG184F | 18.5 | 14.8 | 18.5 | 14.8 | 18.5 | 14.8 | 20 | 20 | 20 | 20 | 20 | 20 | 21.9 | 17.5 | 21.9 | 17.5 | 21.9 | 17.5 | 25.6 | 25.6 | 25.6 | 25.6 | 25.6 | 25.6
DG184G | 21 | 16.8 | 21 | 16.8 | 21 | 16.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 25 | 20 | 25 | 20 | 25 | 20 | 30 | 30 | 30.8 | 30.8 | 30.8 | 30.8
DG184H | 25 | 20 | 25 | 20 | 25 | 20 | 27 | 27 | 27 | 27 | 27 | 27 | 31.3 | 25 | 31.3 | 25 | 31.3 | 25 | 35 | 35 | 35 | 35 | 35 | 35
DG184J | 28 | 22.4 | 28 | 22.4 | 28 | 22.4 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 28 | 35 | 28 | 35 | 28 | 40 | 40 | 40 | 40 | 40 | 40
DG224C | 28 | 22.4 | 28 | 22.4 | 28 | 22.4 | 28 | 28 | 28 | 28 | 28 | 28 | 37.5 | 30 | 37.5 | 30 | 37.5 | 30 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
DG224D | 35 | 28 | 35 | 28 | 35 | 28 | 35 | 35 | 35 | 35 | 35 | 35 | 44 | 35 | 44 | 35 | 44 | 35 | 44 | 44 | 44 | 44 | 44 | 44
DG224E | 40 | 32 | 40 | 32 | 40 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 40 | 50 | 40 | 50 | 40 | 50 | 50 | 50 | 50 | 50 | 50
DG224F | 50 | 40 | 50 | 40 | 50 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 48 | 60 | 48 | 60 | 48 | 60 | 60 | 60 | 60 | 60 | 60
DG224G | 60 | 48 | 60 | 48 | 60 | 48 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 56 | 70 | 56 | 70 | 56 | 75 | 75 | 75 | 75 | 75 | 75
DG274C | 66 | 52.8 | 66 | 52.8 | 66 | 52.8 | 66 | 66 | 66 | 66 | 66 | 66 | 84 | 67 | 84 | 67 | 84 | 67 | 90 | 90 | 90 | 90 | 90 | 90
DG274D | 74 | 59.2 | 74 | 59.2 | 74 | 59.2 | 74 | 74 | 74 | 74 | 74 | 74 | 96 | 77 | 96 | 77 | 96 | 77 | 100 | 100 | 100 | 100 | 100 | 100
DG274E | 94 | 75.2 | 94 | 75.2 | 94 | 75 | 94 | 94 | 94 | 94 | 94 | 94 | 112 | 90 | 112 | 90 | 112 | 90 | 115 | 115 | 115 | 115 | 115 | 115
DG274EL | 100 | 80 | 100 | 80 | 100 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 96 | 120 | 96 | 120 | 96 | 120 | 120 | 120 | 120 | 120 | 120
DG274F | 110 | 88 | 110 | 88 | 110 | 88 | 110 | 110 | 110 | 110 | 110 | 110 | 135 | 108 | 135 | 108 | 135 | 108 | 135 | 135 | 135 | 135 | 135 | 135
DG274G | 120 | 96 | 120 | 96 | 120 | 96 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 120 | 150 | 120 | 150 | 120 | 150 | 150 | 150 | 150 | 150 | 150
DG274H | 140 | 112 | 140 | 112 | 140 | 112 | 140 | 140 | 140 | 140 | 140 | 140 | 156.3 | 125 | 156.3 | 125 | 156.3 | 125 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3
DG274J | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
DG274K | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Notes：
1. The above rating is based on 40 degree C ambient and 125K temperature rising below 1000 meters altitude above sea.

## 2P 3PH rating
Dingol Generator Rating Table (2-pole 3-phase rating)
Model | Three Phase 50Hz 3000PM | [7 empty] | Three Phase 60Hz 3600RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Series Star | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG162D | 12.5 | 10 | 12.5 | 10 | 12.5 | 10 | 12 | 9.6 | 14.7 | 11.8 | 15.6 | 12.5 | 15.6 | 12.5 | 15.6 | 12.5
DG162E | 15 | 12 | 15 | 12 | 15 | 12 | 14.5 | 11.6 | 17.8 | 14.2 | 18.8 | 15 | 18.8 | 15 | 18.8 | 15
DG162F | 17.5 | 14 | 17.5 | 14 | 17.5 | 14 | 16.5 | 13.2 | 20.8 | 16.6 | 21.9 | 17.5 | 21.9 | 17.5 | 21.9 | 17.5
DG162G | 25 | 20 | 25 | 20 | 25 | 20 | 22.5 | 18 | 29.6 | 23.7 | 31.3 | 25 | 31.3 | 25 | 31.3 | 25
DG182H | 30 | 24 | 30 | 24 | 30 | 24 | 27 | 21.6 | 33 | 26.4 | 35 | 28 | 35 | 28 | 35 | 28
DG182J | 35 | 28 | 35 | 28 | 35 | 28 | 30.8 | 24.64 | 37.8 | 30.2 | 40 | 32 | 40 | 32 | 40 | 32
DG182K | 37.5 | 30 | 37.5 | 30 | 37.5 | 30 | 35 | 28 | 44.3 | 35.4 | 46.9 | 37.5 | 46.9 | 37.5 | 46.9 | 37.5
Notes：
1. The above rating is based on 40 degree C ambient and 125K temperature rising below 1000 meters altitude above sea.

## 2P 1PH rating
Dingol Generator Rating Table (2-pole 1-phase rating)
Model | Single Phase 50Hz 3000RPM | [11 empty] | Single Phase 60Hz 3600RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 1 |  | 1 |  | 1 |  | 0.8 |  | 0.8 |  | 0.8 |  | 1 |  | 1 |  | 1
Volts
Series | 220 |  | 230 |  | 240 |  | 220 |  | 230 |  | 240 |  | 220 |  | 230 |  | 240 |  | 220 |  | 230 |  | 240
Parallel | 110 |  | 115 |  | 120 |  | 110 |  | 115 |  | 120 |  | 110 |  | 115 |  | 120 |  | 110 |  | 115 |  | 120
Winding No. | 05 |  | 05 |  | 05 |  | 05 |  | 05 |  | 05 |  | 06 |  | 06 |  | 06 |  | 06 |  | 06 |  | 06
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG162D | 8.4 | 6.7 | 8.4 | 6.7 | 8.4 | 6.7 | 9.6 | 9.6 | 9.6 | 9.6 | 10 | 10 | 10 | 8 | 10 | 8 | 10 | 8 | 11.5 | 11.5 | 11.5 | 11.5 | 12 | 12
DG162E | 10 | 8 | 10 | 8 | 10 | 8 | 11.5 | 11.5 | 11.5 | 11.5 | 12 | 12 | 12.4 | 9.9 | 12.4 | 9.9 | 12.4 | 9.9 | 12.8 | 12.8 | 12.8 | 12.8 | 15 | 15
DG162F | 11.8 | 9.4 | 11.8 | 9.4 | 11.8 | 9.4 | 13.5 | 13.5 | 13.5 | 13.5 | 14.5 | 14.5 | 14.4 | 11.5 | 14.4 | 11.5 | 14.4 | 11.5 | 16.6 | 16.6 | 16.6 | 16.6 | 17.5 | 17.5
DG162G | 16.8 | 13.4 | 16.8 | 13.4 | 16.8 | 13.4 | 17.5 | 17.5 | 18.5 | 18.5 | 19.3 | 19.3 | 20.6 | 16.5 | 20.6 | 16.5 | 20.6 | 16.5 | 23.7 | 23.7 | 23.7 | 23.7 | 22 | 22
DG182H | 20 | 16 | 20 | 16 | 20 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 24.8 | 19.8 | 24.8 | 19.8 | 24.8 | 19.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8
DG182J | 23.5 | 18.8 | 23.5 | 18.8 | 23.5 | 18.8 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 28.9 | 23.1 | 28.9 | 23.1 | 28.9 | 23.1 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9
DG182K | 25 | 20 | 25 | 20 | 25 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 24.8 | 31 | 24.8 | 31 | 24.8 | 31 | 31 | 31 | 31 | 31 | 31
Notes：
1. The above rating is based on 40 degree C ambient and 125K temperature rising below 1000 meters altitude above sea.

## 4P 3PH 40SB (hidden)
Dingol Generator Rating Table (4-pole 3-phase rating)
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 13 |  | 14 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG164B | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG164C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG164D | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG184ES | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG184E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG184F | 29 | 23.2 | 29 | 23.2 | 29 | 23.2 | 23.7 | 18.96 | - | - | - | - | 33.8 | 27.04 | 35 | 28 | 35 | 28 | 37.5 | 30
DG184G | 32.5 | 26 | 32.5 | 26 | 32.5 | 25 | 28.6 | 22.88 | - | - | - | - | 36.3 | 29.04 | 38.8 | 31.04 | 38.8 | 31.04 | 38.8 | 31.04
DG184H | 39 | 31.2 | 39 | 31.2 | 39 | 31.2 | 33.8 | 27.04 | - | - | - | - | 45.9 | 36.72 | 48.5 | 38.8 | 48.5 | 38.8 | 48.5 | 38.8
DG184J | 41.5 | 33.2 | 44 | 35.2 | 41.5 | 33.2 | 36.3 | 29.04 | - | - | - | - | 49.2 | 39.36 | 52 | 41.6 | 52 | 41.6 | 52 | 41.6
DG224C | 45 | 36 | 45 | 36 | 45 | 36 | 31.7 | 25.36 | - | - | 58.1 | 46.48 | 53.1 | 42.48 | 55 | 44 | 55 | 44 | 58.1 | 46.48
DG224D | 53 | 42.4 | 53 | 42.4 | 53 | 42.4 | 39.1 | 31.28 | - | - | 65 | 52 | 62.5 | 50 | 65 | 52 | 65 | 52 | 68.8 | 55.04
DG224E | 61 | 48.8 | 61 | 48.8 | 61 | 48.8 | 45.8 | 36.64 | - | - | 73.8 | 59.04 | 70 | 56 | 73.8 | 59.04 | 73.8 | 59.04 | 78.8 | 63.04
DG224F | 77 | 61.6 | 77 | 61.6 | 77 | 61.6 | 58 | 46.4 | - | - | 89.4 | 71.52 | 88.8 | 71.04 | 92.5 | 74 | 92.5 | 74 | 98.8 | 79.04
DG224G | 87.5 | 70 | 87.5 | 70 | 87.5 | 70 | 76.9 | 61.52 | - | - | 102.5 | 82 | 98.1 | 78.48 | 102.5 | 82 | 102.5 | 82 | 110 | 88
DG274C | 106 | 84.8 | 106 | 84.8 | 106 | 84.8 | - | - | - | - | 127 | 101.6 | 116.3 | 93.04 | 125 | 100 | 117.5 | 94 | 132.5 | 106
DG274D | 130 | 104 | 130 | 104 | 130 | 104 | - | - | - | - | 140 | 112 | 140 | 112 | 150 | 120 | 150 | 120 | 150 | 120
DG274E | 145 | 116 | 145 | 116 | 145 | 116 | - | - | - | - | 170 | 136 | 170 | 136 | 175 | 140 | 175 | 140 | 187.5 | 150
DG274EL | 155 | 124 | 155 | 124 | 155 | 124 | - | - | - | - | - | - | 170 | 136 | 180 | 144 | 180 | 144 | 190 | 152
DG274F | 170 | 136 | 170 | 136 | 170 | 136 | - | - | - | - | 186 | 148.8 | 187.5 | 150 | 200 | 160 | 200 | 160 | 212.5 | 170
DG274G | 187 | 149.6 | 187 | 149.6 | 187 | 149.6 | - | - | - | - | 207.5 | 166 | 213 | 170.4 | 228.8 | 183.04 | 228.8 | 183.04 | 246.8 | 197.44
DG274H | 212 | 169.6 | 212 | 169.6 | 212 | 169.6 | - | - | - | - | 250 | 200 | 237 | 189.6 | 258.8 | 207.04 | 258.8 | 207.04 | 275 | 220
DG274J | 250 | 200 | 250 | 200 | 250 | 200 | - | - | - | - | - | - | 288 | 230.4 | 300 | 240 | 313 | 250.4 | 319 | 255.2
DG274K | 265 | 212 | 265 | 212 | 265 | 212 | - | - | - | - | 319 | 255.2 | 304 | 243.2 | 312.5 | 250 | 331.3 | 265.04 | 331.3 | 265.04
DG444C | 259 | 207.2 | 259 | 207.2 | 259 | 207.2 | 259 | 207.2 | 319 | 255.2 | 319 | 255.2 | 300 | 240 | 313 | 250.4 | 319 | 255.2 | 332 | 265.6
DG444D | 313 | 250.4 | 313 | 250.4 | 313 | 250.4 | 295 | 236 | 375 | 300 | 375 | 300 | 356 | 284.8 | 375 | 300 | 388 | 310.4 | 400 | 320
DGK444D | 320 | 256 | 320 | 256 | 320 | 256 | 310 | 248 | 375 | 300 | 375 | 300 | 363 | 290.4 | 384 | 307.2 | 400 | 320 | 400 | 320
DG444E | 345 | 276 | 345 | 276 | 345 | 276 | 345 | 276 | - | - | - | - | 406 | 324.8 | 419 | 335.2 | 431 | 344.8 | 444 | 355.2
DGK444E | 368 | 294.4 | 368 | 294.4 | 368 | 294.4 | 368 | 294.4 | - | - | - | - | 417 | 333.6 | 442 | 353.6 | 460 | 368 | 460 | 368
DG444F | 390 | 312 | 390 | 312 | 390 | 312 | 390 | 312 | 500 | 400 | 500 | 400 | 475 | 380 | 483 | 386.4 | 488 | 390.4 | 500 | 400
DGK444F | 427 | 341.6 | 427 | 341.6 | 427 | 341.6 | 427 | 341.6 | 535 | 428 | 535 | 428 | 486 | 388.8 | 514 | 411.2 | 535 | 428 | 535 | 428
DG544C | 478 | 382.4 | 478 | 382.4 | 478 | 382.4 | 478 | 382.4 | 520 | 416 | 520 | 416 | 567 | 453.6 | 600 | 480 | 625 | 500 | 625 | 500
DG544D | 515 | 412 | 515 | 412 | 515 | 412 | 515 | 412 | 655 | 524 | 655 | 524 | 610 | 488 | 646 | 516.8 | 673 | 538.4 | 673 | 538.4
DG544ES | 600 | 480 | 600 | 480 | 600 | 480 | 600 | 480 | - | - | - | - | 635 | 508 | 650 | 520 | 670 | 536 | 700 | 560
DG544E | 636 | 508.8 | 636 | 508.8 | 636 | 508.8 | 636 | 508.8 | 710 | 568 | 710 | 568 | 726 | 580.8 | 768 | 614.4 | 800 | 640 | 800 | 640
DG544EL | 650 | 520 | 650 | 520 | 650 | 520 | 650 | 520 | 750 | 600 | 750 | 600 | 700 | 560 | 735 | 588 | 755 | 604 | 765 | 612
DG544F | 710 | 568 | 710 | 568 | 710 | 568 | 690 | 552 | 875 | 700 | 875 | 700 | 825 | 660 | 873 | 698.4 | 909 | 727.2 | 909 | 727.2
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 13 |  | 14 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG634B | 730 | 584 | 775 | 620 | 775 | 620 | 700 | 560 | 968 | 774.4 | 968 | 774.4 | 840 | 672 | 889 | 711.2 | 929 | 743.2 | 970 | 776
DG634C1 | 785 | 628 | 825 | 660 | 825 | 660 | 745 | 596 | - | - | - | - | 897 | 717.6 | 948 | 758.4 | 992 | 793.6 | 1035 | 828
DG634D | 890 | 712 | 938 | 750.4 | 938 | 750.4 | 850 | 680 | 1097 | 877.6 | 1097 | 877.6 | 1018 | 814.4 | 1077 | 861.6 | 1126 | 900.8 | 1175 | 940
DG634E | 980 | 784 | 1030 | 824 | 1030 | 824 | 938 | 750.4 | 1290 | 1032 | 1290 | 1032 | 1118 | 894.4 | 1180 | 944 | 1236 | 988.8 | 1290 | 1032
DG634F | 1125 | 900 | 1165 | 932 | 1165 | 932 | 1055 | 844 | 1362 | 1089.6 | 1362 | 1089.6 | 1243 | 994.4 | 1315 | 1052 | 1375 | 1100 | 1435 | 1148
DG634G | 1190 | 952 | 1288 | 1030.4 | 1288 | 1030.4 | 1170 | 936 | 1613 | 1290.4 | - | - | 1354 | 1083.2 | 1432 | 1145.6 | 1497 | 1197.6 | 1563 | 1250.4
0
DH634G | 810 | 648 | 810 | 648 | 810 | 648 |  |  |  | 0 |  |  | 875 | 700 | 925 | 740 | 963 | 770.4 | 1000 | 800
DH634H | 940 | 752 | 940 | 752 | 940 | 752 |  |  |  | 0 |  |  | 1025 | 820 | 1063 | 850.4 | 1075 | 860 | 1125 | 900
DH634J | 1030 | 824 | 1030 | 824 | 1030 | 824 |  |  |  | 0 |  |  | 1150 | 920 | 1200 | 960 | 1250 | 1000 | 1200 | 960
DH634K | 1130 | 904 | 1130 | 904 | 1130 | 904 |  |  |  | 0 |  |  | 1275 | 1020 | 1338 | 1070.4 | 1388 | 1110.4 | 1438 | 1150.4
Notes：
1. DG634C has no W11 option
2. DGK-foluted fan
3. The above rating is based on 40 degree C ambient and 125K temperature rising below 1000 meters altitude above sea.

## 4P 3PH 27SB (hidden)
Dingol Generator Rating Table (4-pole 3-phase rating)
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 13 |  | 14 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG164B | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG164C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG164D | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG184ES | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG184E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DG184F | 30 | 24 | 30 | 24 | 30 | 24 | 24.5 | 19.6 | - | - | - | - | 34.4 | 27.52 | 35.6 | 28.48 | 35.6 | 28.48 | 38.8 | 31.04
DG184G | 33 | 26.4 | 33 | 26.4 | 33 | 25 | 29 | 23.2 | - | - | - | - | 36.9 | 29.52 | 40 | 32 | 40 | 32 | 40 | 32
DG184H | 40 | 32 | 40 | 32 | 40 | 32 | 34.7 | 27.76 | - | - | - | - | 47.3 | 37.84 | 50 | 40 | 50 | 40 | 50 | 40
DG184J | 42.5 | 34 | 42.5 | 34 | 42.5 | 34 | 37.2 | 29.76 | - | - | - | - | 50.6 | 40.48 | 53.5 | 42.8 | 53.5 | 42.8 | 53.5 | 42.8
DG224C | 46.8 | 37.44 | 46.8 | 37.44 | 46.8 | 37.44 | 33 | 26.4 | - | - | 60 | 48 | 55 | 44 | 56.3 | 45.04 | 56.3 | 45.04 | 60 | 48
DG224D | 55 | 44 | 55 | 44 | 55 | 44 | 41.2 | 32.96 | - | - | 66.3 | 53.04 | 65 | 52 | 66.3 | 53.04 | 66.3 | 53.04 | 71.3 | 57.04
DG224E | 63 | 50.4 | 63 | 50.4 | 63 | 50.4 | 47.3 | 37.84 | - | - | 75 | 60 | 72.5 | 58 | 75 | 60 | 75 | 60 | 80 | 64
DG224F | 80 | 64 | 80 | 64 | 80 | 64 | 60.4 | 48.32 | - | - | 92 | 73.6 | 91.9 | 73.52 | 95 | 76 | 95 | 76 | 102.5 | 82
DG224G | 90.8 | 72.64 | 90.8 | 72.64 | 90.8 | 72.64 | 80.1 | 64.08 | - | - | 106.3 | 85.04 | 101.3 | 81.04 | 106.3 | 85.04 | 106.3 | 85.04 | 113.8 | 91.04
DG274C | 110 | 88 | 110 | 88 | 110 | 88 | - | - | - | - | 132 | 105.6 | 120 | 96 | 127.5 | 102 | 127.5 | 102 | 137.5 | 110
DG274D | 135 | 108 | 135 | 108 | 135 | 108 | - | - | - | - | 140 | 112 | 140 | 112 | 150 | 120 | 150 | 120 | 150 | 120
DG274E | 150 | 120 | 150 | 120 | 150 | 120 | - | - | - | - | 175 | 140 | 175 | 140 | 181.3 | 145.04 | 181.3 | 145.04 | 193.8 | 155.04
DG274EL | 160 | 128 | 160 | 128 | 160 | 128 | - | - | - | - | - | - | 170 | 136 | 180 | 144 | 180 | 144 | 190 | 152
DG274F | 175 | 140 | 175 | 140 | 175 | 140 | - | - | - | - | 190 | 152 | 192.5 | 154 | 206.3 | 165.04 | 206.3 | 165.04 | 218.8 | 175.04
DG274G | 194 | 155.2 | 194 | 155.2 | 194 | 155.2 | - | - | - | - | 212.5 | 170 | 218.5 | 174.8 | 234 | 187.2 | 234 | 187.2 | 253.3 | 202.64
DG274H | 220 | 176 | 220 | 176 | 220 | 176 | - | - | - | - | 256.3 | 205.04 | 256.3 | 205.04 | 265 | 212 | 265 | 212 | 280 | 224
DG274J | 260 | 208 | 260 | 208 | 260 | 208 | - | - | - | - | - | - | 294 | 235.2 | 306 | 244.8 | 319 | 255.2 | 325 | 260
DG274K | 275 | 220 | 275 | 220 | 275 | 220 | - | - | - | - | 325 | 260 | 312 | 249.6 | 320 | 256 | 343.8 | 275.04 | 343.8 | 275.04
DG444C | 268 | 214.4 | 268 | 214.4 | 268 | 214.4 | 268 | 214.4 | 331 | 264.8 | 331 | 264.8 | 313 | 250.4 | 325 | 260 | 331 | 264.8 | 344 | 275.2
DG444D | 324 | 259.2 | 324 | 259.2 | 324 | 259.2 | 305 | 244 | 383 | 306.4 | 383 | 306.4 | 363 | 290.4 | 383 | 306.4 | 398 | 318.4 | 413 | 330.4
DGK444D | 330 | 264 | 330 | 264 | 330 | 264 | 320 | 256 | 383 | 306.4 | 383 | 306.4 | 374 | 299.2 | 396 | 316.8 | 413 | 330.4 | 413 | 330.4
DG444E | 358 | 286.4 | 358 | 286.4 | 358 | 286.4 | 358 | 286.4 | - | - | - | - | 419 | 335.2 | 431 | 344.8 | 444 | 355.2 | 456 | 364.8
DGK444E | 380 | 304 | 380 | 304 | 380 | 304 | 380 | 304 | - | - | - | - | 432 | 345.6 | 456 | 364.8 | 475 | 380 | 475 | 380
DG444F | 404 | 323.2 | 404 | 323.2 | 404 | 323.2 | 404 | 323.2 | 519 | 415.2 | 519 | 415.2 | 488 | 390.4 | 500 | 400 | 506 | 404.8 | 519 | 415.2
DGK444F | 440 | 352 | 440 | 352 | 440 | 352 | 440 | 352 | 550 | 440 | 550 | 440 | 500 | 400 | 528 | 422.4 | 550 | 440 | 550 | 440
DG544C | 495 | 396 | 495 | 396 | 495 | 396 | 495 | 396 | 540 | 432 | 540 | 432 | 569 | 455.2 | 600 | 480 | 631 | 504.8 | 644 | 515.2
DG544D | 530 | 424 | 530 | 424 | 530 | 424 | 530 | 424 | 673 | 538.4 | 673 | 538.4 | 606 | 484.8 | 644 | 515.2 | 673 | 538.4 | 694 | 555.2
DG544ES | 620 | 496 | 620 | 496 | 620 | 496 | 620 | 496 | - | - | - | - | 635 | 508 | 650 | 520 | 670 | 536 | 700 | 560
DG544E | 660 | 528 | 660 | 528 | 660 | 528 | 660 | 528 | 730 | 584 | 730 | 584 | 738 | 590.4 | 769 | 615.2 | 798 | 638.4 | 819 | 655.2
DG544EL | 680 | 544 | 680 | 544 | 680 | 544 | 680 | 544 | 750 | 600 | 750 | 600 | 700 | 560 | 735 | 588 | 755 | 604 | 765 | 612
DG544F | 738 | 590.4 | 738 | 590.4 | 738 | 590.4 | 715 | 572 | 906 | 724.8 | 906 | 724.8 | 806 | 644.8 | 844 | 675.2 | 878 | 702.4 | 906 | 724.8
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 13 |  | 14 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG634B | 745 | 596 | 790 | 632 | 790 | 632 | 715 | 572 | 984 | 787.2 | 984 | 787.2 | 849 | 679.2 | 898 | 718.4 | 939 | 751.2 | 980 | 784
DG634C1 | 800 | 640 | 840 | 672 | 840 | 672 | 760 | 608 | - | - | - | - | 905 | 724 | 958 | 766.4 | 1000 | 800 | 1045 | 836
DG634D | 910 | 728 | 955 | 764 | 955 | 764 | 865 | 692 | 1116 | 892.8 | 1116 | 892.8 | 1030 | 824 | 1090 | 872 | 1140 | 912 | 1190 | 952
DG634E | 1000 | 800 | 1050 | 840 | 1050 | 840 | 955 | 764 | 1313 | 1050.4 | 1313 | 1050.4 | 1130 | 904 | 1195 | 956 | 1250 | 1000 | 1305 | 1044
DG634F | 1145 | 916 | 1185 | 948 | 1185 | 948 | 1075 | 860 | 1386 | 1108.8 | 1386 | 1108.8 | 1257 | 1005.6 | 1329 | 1063.2 | 1390 | 1112 | 1450 | 1160
DG634G | 1250 | 1000 | 1313 | 1050.4 | 1313 | 1050.4 | 1190 | 952 | 1641 | 1312.8 | - | - | 1369 | 1095.2 | 1448 | 1158.4 | 1514 | 1211.2 | 1580 | 1264
DH634G | 810 | 648 | 810 | 648 | 810 | 648 | [6 empty] | 875 | 700 | 925 | 740 | 963 | 770.4 | 1000 | 800
DH634H | 940 | 752 | 940 | 752 | 940 | 752 | [6 empty] | 1025 | 820 | 1063 | 850.4 | 1075 | 860 | 1125 | 900
DH634J | 1030 | 824 | 1030 | 824 | 1030 | 824 | [6 empty] | 1150 | 920 | 1200 | 960 | 1250 | 1000 | 1200 | 960
DH634K | 1130 | 904 | 1130 | 904 | 1130 | 904 | [6 empty] | 1275 | 1020 | 1338 | 1070.4 | 1388 | 1110.4 | 1438 | 1150.4
Notes：
1. DG634C has no W11 option
2. DGK-foluted fan
3. The above rating is based on 40 degree C ambient and 125K temperature rising below 1000 meters altitude above sea.

## 4P 3PH 150K
Dingol Generator Rating Table (4-pole 3-phase rating)
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  |  |  | 110-120 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 13 |  | 14 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG164B | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG164C | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG164D | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG184ES | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG184E | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG184F | 29 | 23.2 | 29 | 23.2 | 29 | 23.2 | 23.7 | 18.96 |  |  | 33.475 | 26.78 | 33.8 | 27.04 | 35 | 28 | 35 | 28 | 37.5 | 30
DG184G | 32.5 | 26 | 32.5 | 26 | 32.5 | 26 | 28.6 | 22.88 |  |  | 38.625 | 30.9 | 36.3 | 29.04 | 38.8 | 31.04 | 38.8 | 31.04 | 38.8 | 31.04
DG184H | 39 | 31.2 | 39 | 31.2 | 39 | 31.2 | 33.8 | 27.04 |  |  | 44.805 | 35.844 | 45.9 | 36.72 | 48.5 | 38.8 | 48.5 | 38.8 | 48.5 | 38.8
DG184J | 41.5 | 33.2 | 44 | 35.2 | 41.5 | 33.2 | 36.3 | 29.04 |  |  | 48.925 | 39.14 | 49.2 | 39.36 | 52 | 41.6 | 52 | 41.6 | 52 | 41.6
DG224C | 45 | 36 | 45 | 36 | 45 | 36 | 31.7 | 25.36 |  |  | 58.1 | 46.48 | 53.1 | 42.48 | 55 | 44 | 55 | 44 | 58.1 | 46.48
DG224D | 53 | 42.4 | 53 | 42.4 | 53 | 42.4 | 39.1 | 31.28 |  |  | 65 | 52 | 62.5 | 50 | 65 | 52 | 65 | 52 | 68.8 | 55.04
DG224E | 61 | 48.8 | 61 | 48.8 | 61 | 48.8 | 45.8 | 36.64 |  |  | 73.8 | 59.04 | 70 | 56 | 73.8 | 59.04 | 73.8 | 59.04 | 78.8 | 63.04
DG224F | 77 | 61.6 | 77 | 61.6 | 77 | 61.6 | 58 | 46.4 |  |  | 89.4 | 71.52 | 88.8 | 71.04 | 92.5 | 74 | 92.5 | 74 | 98.8 | 79.04
DG224G | 87.5 | 70 | 87.5 | 70 | 87.5 | 70 | 76.9 | 61.52 |  |  | 102.5 | 82 | 98.1 | 78.48 | 102.5 | 82 | 102.5 | 82 | 110 | 88
DG274C | 106 | 84.8 | 106 | 84.8 | 106 | 84.8 | - | - |  |  | 127 | 101.6 | 116.3 | 93.04 | 125 | 100 | 125 | 100 | 132.5 | 106
DG274D | 130 | 104 | 130 | 104 | 130 | 104 | - | - |  |  | 145 | 116 | 145 | 116 | 155 | 124 | 155 | 124 | 160 | 128
DG274E | 145 | 116 | 145 | 116 | 145 | 116 | - | - |  |  | 170 | 136 | 170 | 136 | 175 | 140 | 175 | 140 | 187.5 | 150
DG274EL | 154.5 | 123.6 | 154.5 | 123.6 | 154.5 | 123.6 | - | - |  |  | 175.1 | 140.08 | 175.1 | 140.08 | 185.4 | 148.32 | 185.4 | 148.32 | 195.7 | 156.56
DG274F | 170 | 136 | 170 | 136 | 170 | 136 | - | - |  |  | 186 | 148.8 | 187.5 | 150 | 200 | 160 | 200 | 160 | 212.5 | 170
DG274G | 187 | 149.6 | 187 | 149.6 | 187 | 149.6 | - | - |  |  | 207.5 | 166 | 213 | 170.4 | 228.8 | 183.04 | 228.8 | 183.04 | 246.8 | 197.44
DG274H | 212 | 169.6 | 212 | 169.6 | 212 | 169.6 | - | - |  |  | 250 | 200 | 250 | 200 | 258.8 | 207.04 | 258.8 | 207.04 | 275 | 220
DG274J | 250 | 200 | 250 | 200 | 250 | 200 | - | - |  |  | 292 | 233.6 | 288 | 230.4 | 300 | 240 | 313 | 250.4 | 319 | 255.2
DG274K | 265 | 212 | 265 | 212 | 265 | 212 | - | - |  |  | 319 | 255.2 | 304 | 243.2 | 312.5 | 250 | 331.3 | 265.04 | 331.3 | 265.04
DG444C | 259 | 207.2 | 259 | 207.2 | 259 | 207.2 | 259 | 207.2 | 319 | 255.2 | 319 | 255.2 | 300 | 240 | 313 | 250.4 | 319 | 255.2 | 332 | 265.6
DG444D | 313 | 250.4 | 313 | 250.4 | 313 | 250.4 | 295 | 236 | 375 | 300 | 375 | 300 | 356 | 284.8 | 375 | 300 | 388 | 310.4 | 400 | 320
DGK444D | 320 | 256 | 320 | 256 | 320 | 256 | 310 | 248 | 380 | 304 | 380 | 304 | 363 | 290.4 | 384 | 307.2 | 400 | 320 | 400 | 320
DG444E | 345 | 276 | 345 | 276 | 345 | 276 | 345 | 276 | - | - | - | - | 406 | 324.8 | 419 | 335.2 | 431 | 344.8 | 444 | 355.2
DGK444E | 368 | 294.4 | 368 | 294.4 | 368 | 294.4 | 368 | 294.4 | - | - | - | - | 417 | 333.6 | 442 | 353.6 | 460 | 368 | 460 | 368
DG444F | 390 | 312 | 390 | 312 | 390 | 312 | 390 | 312 | 500 | 400 | - | - | 475 | 380 | 483 | 386.4 | 488 | 390.4 | 500 | 400
DGK444F | 415 | 332 | 415 | 332 | 415 | 332 | 415 | 332 | 535 | 428 | - | - | 486 | 388.8 | 508 | 406.4 | 513 | 410.4 | 525 | 420
DG544C | 478 | 382.4 | 478 | 382.4 | 478 | 382.4 | 478 | 382.4 | 520 | 416 | 520 | 416 | 550 | 440 | 581 | 464.8 | 613 | 490.4 | 625 | 500
DG544D | 515 | 412 | 515 | 412 | 515 | 412 | 515 | 412 | 655 | 524 | 655 | 524 | 588 | 470.4 | 625 | 500 | 655 | 524 | 675 | 540
DG544ES | 579.89 | 463.912 | 579.89 | 463.912 | 579.89 | 463.912 | 579.89 | 463.912 | 669.5 | 535.6 | 669.5 | 535.6 | 643.75 | 515 | 669.5 | 535.6 | 700 | 560 | 725 | 580
DG544E | 636 | 508.8 | 636 | 508.8 | 636 | 508.8 | 636 | 508.8 | 710 | 568 | 710 | 568 | 719 | 575.2 | 750 | 600 | 780 | 624 | 800 | 640
DG544EL | 650 | 520 | 650 | 520 | 650 | 520 | 650 | 520 | 731.3 | 585.04 | 731.3 | 585.04 | 728 | 582.4 | 765 | 612 | 800 | 640 | 825 | 660
DG544F | 710 | 568 | 710 | 568 | 710 | 568 | 690 | 552 | 850 | 680 | 850 | 680 | 781 | 624.8 | 819 | 655.2 | 848 | 678.4 | 875 | 700
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 13 |  | 14 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG634B | 731.3 | 585.04 | 772.5 | 618 | 772.5 | 618 | 700.4 | 560.32 | 966.14 | 772.912 | 966.14 | 772.912 | 834.3 | 667.44 | 880.65 | 704.52 | 921.85 | 737.48 | 966.14 | 772.912
DG634C1 | 782.8 | 626.24 | 824 | 659.2 | 824 | 659.2 | 746.75 | 597.4 | - | - | - | - | 890.95 | 712.76 | 943.48 | 754.784 | 986.74 | 789.392 | 1030 | 824
DG634D | 890.95 | 712.76 | 937.3 | 749.84 | 937.3 | 749.84 | 849.75 | 679.8 | 1094.89 | 875.912 | 1094.89 | 875.912 | 1015.58 | 812.464 | 1065.02 | 852.016 | 1122.7 | 898.16 | 1172.14 | 937.712
DG634E | 978.5 | 782.8 | 1030 | 824 | 1030 | 824 | 937.3 | 749.84 | 1287.5 | 1030 | 1287.5 | 1030 | 1115.49 | 892.392 | 1179.35 | 943.48 | 1232.91 | 986.328 | 1287.5 | 1030
DG634F | 1122.7 | 898.16 | 1163.9 | 931.12 | 1163.9 | 931.12 | 1055.75 | 844.6 | 1359.6 | 1087.68 | 1359.6 | 1087.68 | 1240.12 | 992.096 | 1312.22 | 1049.776 | 1371.96 | 1097.568 | 1431.7 | 1145.36
DG634G | 1225.7 | 980.56 | 1287.5 | 1030 | 1287.5 | 1030 | 1169.05 | 935.24 | 1545 | 1236 | - | - | 1349.3 | 1079.44 | 1427.58 | 1142.064 | 1492.47 | 1193.976 | 1558.39 | 1246.712
DG734B | 1400.8 | 1120.64 | 1442 | 1153.6 | 1442 | 1153.6 | 1416.25 | 1133 | 1625 | 1300 | - | - | 1570.75 | 1256.6 | 1673.75 | 1339 | 1704.65 | 1363.72 | 1740.7 | 1392.56
DG734C | 1550.15 | 1240.12 | 1596.5 | 1277.2 | 1596.5 | 1277.2 | 1565.6 | 1252.48 | 1845 | 1476 | - | - | 1756.15 | 1404.92 | 1869.45 | 1495.56 | 1910.65 | 1528.52 | 1946.7 | 1557.36
DG734D | 1663.45 | 1330.76 | 1699.5 | 1359.6 | 1699.5 | 1359.6 | 1668.6 | 1334.88 | 1995 | 1596 | - | - | 1869.45 | 1495.56 | 1993.05 | 1594.44 | 2034.25 | 1627.4 | 2075.45 | 1660.36
DG734E | 1900.35 | 1520.28 | 1957 | 1565.6 | 1957 | 1565.6 | 1920.95 | 1536.76 | - | - | - | - | 2132.1 | 1705.68 | 2276.3 | 1821.04 | 2317.5 | 1854 | 2369 | 1895.2
DG734F | 2080.6 | 1664.48 | 2142.4 | 1713.92 | 2142.4 | 1713.92 | 2101.2 | 1680.96 | 2605 | 2084 | - | - | 2415.35 | 1932.28 | 2575 | 2060 | 2626.5 | 2101.2 | 2678 | 2142.4
DG734G | 2199.05 | 1759.24 | 2266 | 1812.8 | 2266 | 1812.8 | 2224.8 | 1779.84 | - | - | - | - | 2492.6 | 1994.08 | 2611.05 | 2088.84 | 2703.75 | 2163 | 2832.5 | 2266
DG734H | 2338.1 | 1870.48 | 2410.2 | 1928.16 | 2410.2 | 1928.16 | 2369 | 1895.2 | - | - | - | - | 2600.75 | 2080.6 | 2719.2 | 2175.36 | 2806.75 | 2245.4 | 2914.9 | 2331.92
Notes：
1. DG634C has no W11 option
2. DGK-foluted fan
3. The above rating is based on 40 degree C ambient and 150K temperature rising below 1000 meters altitude above sea.
4. DG734B～H has only W12 option

## 4P 3PH 163K
Dingol Generator Rating Table (4-pole 3-phase rating)
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  |  |  | 110-120 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 13 |  | 14 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG164B | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG164C | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG164D | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG184ES | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG184E | - | - | - | - | - | - | - | - |  |  | - | - | - | - | - | - | - | - | - | -
DG184F | 30 | 24 | 30 | 24 | 30 | 24 | 24.5 | 19.6 | - | - | 34.125 | 27.3 | 34.4 | 27.52 | 35.6 | 28.48 | 35.6 | 22.784 | 38.8 | 31.04
DG184G | 33 | 26.4 | 33 | 26.4 | 33 | 26.4 | 29 | 23.2 | - | - | 39.375 | 31.5 | 36.9 | 29.52 | 40 | 32 | 40 | 25.6 | 40 | 32
DG184H | 40 | 32 | 40 | 32 | 40 | 32 | 34.7 | 27.76 | - | - | 45.675 | 36.54 | 47.3 | 37.84 | 50 | 40 | 50 | 32 | 50 | 40
DG184J | 42.5 | 34 | 45 | 36 | 42.5 | 34 | 37.2 | 29.76 | - | - | 49.875 | 39.9 | 50.6 | 40.48 | 53.5 | 42.8 | 53.5 | 34.24 | 53.5 | 42.8
DG224C | 46.8 | 37.44 | 46.8 | 37.44 | 46.8 | 37.44 | 33 | 26.4 | - | - | 60 | 48 | 55 | 44 | 56.3 | 45.04 | 56.3 | 45.04 | 60 | 48
DG224D | 55 | 44 | 55 | 44 | 55 | 44 | 41.2 | 32.96 | - | - | 66.3 | 53.04 | 65 | 52 | 66.3 | 53.04 | 66.3 | 53.04 | 71.3 | 57.04
DG224E | 63 | 50.4 | 63 | 50.4 | 63 | 50.4 | 47.3 | 37.84 | - | - | 75 | 60 | 72.5 | 58 | 75 | 60 | 75 | 60 | 80 | 64
DG224F | 80 | 64 | 80 | 64 | 80 | 64 | 60.4 | 48.32 | - | - | 92 | 73.6 | 91.9 | 73.52 | 95 | 76 | 95 | 76 | 102.5 | 82
DG224G | 90.8 | 72.64 | 90.8 | 72.64 | 90.8 | 72.64 | 80.1 | 64.08 | - | - | 106.3 | 85.04 | 101.3 | 81.04 | 106.3 | 85.04 | 106.3 | 85.04 | 113.8 | 91.04
DG274C | 110 | 88 | 110 | 88 | 110 | 88 | - | - | - | - | 132 | 105.6 | 120 | 96 | 127.5 | 102 | 127.5 | 102 | 137.5 | 110
DG274D | 132.5 | 106 | 132.5 | 106 | 132.5 | 106 | - | - | - | - | 150 | 120 | 150 | 120 | 160 | 128 | 160 | 128 | 160 | 128
DG274E | 150 | 120 | 150 | 120 | 150 | 120 | - | - | - | - | 175 | 140 | 175 | 140 | 181.3 | 145.04 | 181.3 | 145.04 | 193.8 | 155.04
DG274EL | 157.5 | 126 | 157.5 | 126 | 157.5 | 126 |  |  | - | - |  |  |  | 0 |  | 0 |  | 0 |  | 0
DG274F | 175 | 140 | 175 | 140 | 175 | 140 | - | - | - | - | 190 | 152 | 192.5 | 154 | 206.3 | 165.04 | 206.3 | 165.04 | 218.8 | 175.04
DG274G | 194 | 155.2 | 194 | 155.2 | 194 | 155.2 | - | - | - | - | 212.5 | 170 | 218.5 | 174.8 | 234 | 187.2 | 234 | 187.2 | 253.3 | 202.64
DG274H | 220 | 176 | 220 | 176 | 220 | 176 | - | - | - | - | 256.3 | 205.04 | 256.3 | 205.04 | 265 | 212 | 265 | 212 | 280 | 224
DG274J | 260 | 208 | 260 | 208 | 260 | 208 | - | - | - | - | 300 | 240 | 294 | 235.2 | 306 | 244.8 | 319 | 255.2 | 325 | 260
DG274K | 275 | 220 | 275 | 220 | 275 | 220 | - | - | - | - | 325 | 260 | 312 | 249.6 | 320 | 256 | 343.8 | 275.04 | 343.8 | 275.04
DG444C | 268 | 214.4 | 268 | 214.4 | 268 | 214.4 | 268 | 214.4 | 330 | 264 | 330 | 264 | 313 | 250.4 | 325 | 260 | 331 | 264.8 | 344 | 275.2
DG444D | 324 | 259.2 | 324 | 259.2 | 324 | 259.2 | 305 | 244 | 380 | 304 | 380 | 304 | 363 | 290.4 | 383 | 306.4 | 398 | 318.4 | 413 | 330.4
DGK444D | 330 | 264 | 330 | 264 | 330 | 264 | 320 | 256 | 385 | 308 | 385 | 308 | 374 | 299.2 | 396 | 316.8 | 413 | 330.4 | 413 | 330.4
DG444E | 358 | 286.4 | 358 | 286.4 | 358 | 286.4 | 358 | 286.4 | - | - | - | - | 419 | 335.2 | 431 | 344.8 | 444 | 355.2 | 456 | 364.8
DGK444E | 375 | 300 | 375 | 300 | 375 | 300 | 375 | 300 | - | - | - | - | 432 | 345.6 | 456 | 364.8 | 475 | 380 | 475 | 380
DG444F | 404 | 323.2 | 404 | 323.2 | 404 | 323.2 | 404 | 323.2 | 519 | 415.2 | - | - | 488 | 390.4 | 500 | 400 | 506 | 404.8 | 519 | 415.2
DGK444F | 425 | 340 | 425 | 340 | 425 | 340 | 425 | 340 | 550 | 440 | - | - | 500 | 400 | 528 | 422.4 | 550 | 440 | 550 | 440
DG544C | 495 | 396 | 495 | 396 | 495 | 396 | 495 | 396 | 540 | 432 | 540 | 432 | 569 | 455.2 | 600 | 480 | 631 | 504.8 | 644 | 515.2
DG544D | 530 | 424 | 530 | 424 | 530 | 424 | 530 | 424 | 673 | 538.4 | 673 | 538.4 | 606 | 484.8 | 644 | 515.2 | 673 | 538.4 | 694 | 555.2
DG544ES | 600 | 480 | 600 | 480 | 600 | 480 | 600 | 480 | 700 | 560 | 700 | 560 | 688 | 550.4 | 720 | 576 | 740 | 592 | 760 | 608
DG544E | 660 | 528 | 660 | 528 | 660 | 528 | 660 | 528 | 730 | 584 | 730 | 584 | 738 | 590.4 | 769 | 615.2 | 798 | 638.4 | 819 | 655.2
DG544EL | 675 | 540 | 675 | 540 | 675 | 540 | 675 | 540 | 750 | 600 | 750 | 600 | 750 | 600 | 780 | 624 | 813 | 650.4 | 830 | 664
DG544F | 738 | 590.4 | 738 | 590.4 | 738 | 590.4 | 715 | 572 | 906 | 724.8 | 906 | 724.8 | 850 | 680 | 900 | 720 | 938 | 750.4 | 906 | 724.8
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 13 |  | 14 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG634B | 745.5 | 596.4 | 787.5 | 630 | 787.5 | 630 | 714 | 571.2 | 984.9 | 787.5 | 984.9 | 787.5 | 850.5 | 680.4 | 897.75 | 718.2 | 939.75 | 751.8 | 984.9 | 787.92
DG634C1 | 798 | 638.4 | 840 | 672 | 840 | 672 | 761.25 | 609 | - | - | - | - | 908.25 | 726.6 | 961.8 | 769.44 | 1005.9 | 804.72 | 1050 | 840
DG634D | 908.25 | 726.6 | 955.5 | 764.4 | 955.5 | 764.4 | 866.25 | 693 | 1116.15 | 892.5 | 1116.15 | 892.5 | 1035.3 | 828.24 | 1085.7 | 868.56 | 1144.5 | 915.6 | 1194.9 | 955.92
DG634E | 997.5 | 798 | 1050 | 840 | 1050 | 840 | 955.5 | 764.4 | 1312.5 | 1050 | 1312.5 | 1050 | 1137.15 | 909.72 | 1202.25 | 961.8 | 1256.85 | 1005.48 | 1312.5 | 1050
DG634F | 1144.5 | 915.6 | 1186.5 | 949.2 | 1186.5 | 949.2 | 1076.25 | 861 | 1386 | 1108.8 | 1386 | 1108.8 | 1264.2 | 1011.36 | 1337.7 | 1070.16 | 1398.6 | 1118.88 | 1459.5 | 1167.6
DG634G | 1249.5 | 999.6 | 1312.5 | 1050 | 1312.5 | 1050 | 1191.75 | 953.4 | 1575 | 1260 | - | - | 1375.5 | 1100.4 | 1455.3 | 1164.24 | 1521.45 | 1217.16 | 1588.65 | 1270.92
DG734B | 1428 | 1142.4 | 1470 | 1176 | 1470 | 1176 | 1443.75 | 1155 | 1638 | 1310.4 | - | - | 1601.25 | 1281 | 1706.25 | 1365 | 1737.75 | 1390.2 | 1774.5 | 1419.6
DG734C | 1580.25 | 1264.2 | 1627.5 | 1302 | 1627.5 | 1302 | 1596 | 1276.8 | 1858.5 | 1486.8 | - | - | 1790.25 | 1432.2 | 1905.75 | 1524.6 | 1947.75 | 1558.2 | 1984.5 | 1587.6
DG734D | 1695.75 | 1356.6 | 1732.5 | 1386 | 1732.5 | 1386 | 1701 | 1360.8 | 2010.75 | 1608.6 | - | - | 1905.75 | 1524.6 | 2031.75 | 1625.4 | 2073.75 | 1659 | 2115.75 | 1692.6
DG734E | 1937.25 | 1549.8 | 1995 | 1596 | 1995 | 1596 | 1958.25 | 1566.6 | - | - | - | - | 2173.5 | 1738.8 | 2320.5 | 1856.4 | 2362.5 | 1890 | 2415 | 1932
DG734F | 2121 | 1696.8 | 2184 | 1747.2 | 2184 | 1747.2 | 2142 | 1713.6 | 2625 | 2100 | - | - | 2462.25 | 1969.8 | 2625 | 2100 | 2677.5 | 2142 | 2730 | 2184
DG734G | 2241.75 | 1793.4 | 2310 | 1848 | 2310 | 1848 | 2268 | 1814.4 | - | - | - | - | 2541 | 2032.8 | 2661.75 | 2129.4 | 2756.25 | 2205 | 2887.5 | 2310
DG734H | 2383.5 | 1906.8 | 2457 | 1965.6 | 2457 | 1965.6 | 2415 | 1932 | - | - | - | - | 2651.25 | 2121 | 2772 | 2217.6 | 2861.25 | 2289 | 2971.5 | 2377.2
Notes：
1. DG634C has no W11 option
2. DGK-foluted fan
3. The above rating is based on 27 degree C ambient and 163K temperature rising below 1000 meters altitude above sea.
4. DG734B～H has only W12 option

## 4P 3PH 1 Hour
Dingol Generator Rating Table (4-pole 3-phase rating)
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  |  |  | 110-120 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 13 |  | 14 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG164A | 8.91 | 7.15 | 8.91 | 7.15 | 8.91 | 7.15 | 6.82 | 5.456 | - | - | 10.56 | 8.47 | 10.56 | 8.47 | 11.22 | 9.02 | 11.22 | 9.02 | 11.22 | 9.02
DG164B | 12.1 | 9.68 | 12.1 | 9.68 | 12.1 | 9.68 | 9.24 | 7.392 | - | - | 14.3 | 11.44 | 14.3 | 11.44 | 15.18 | 12.1 | 15.18 | 12.1 | 15.18 | 12.1
DG164C | 14.85 | 11.88 | 14.85 | 11.88 | 14.85 | 11.88 | 12.1 | 9.68 | - | - | 17.6 | 14.08 | 17.6 | 14.08 | 18.59 | 14.85 | 18.59 | 14.85 | 18.59 | 14.85
DG164D | 17.6 | 14.08 | 17.6 | 14.08 | 17.6 | 14.08 | 14.85 | 11.88 | - | - | 22 | 17.6 | 20.79 | 16.61 | 22 | 17.6 | 22 | 17.6 | 22 | 17.6
DG184ES | 22 | 17.6 | 22 | 17.6 | 22 | 17.6 | 16.5 | 13.2 | - | - | 27.5 | 22 | 26.4 | 21.12 | 27.5 | 22 | 27.5 | 22 | 27.5 | 22
DG184E | 24.75 | 19.8 | 24.75 | 19.8 | 24.75 | 19.8 | 19.25 | 15.4 | - | - | 30.25 | 24.2 | 30.25 | 24.2 | 31.68 | 25.3 | 31.68 | 25.3 | 33 | 26.4
DG184F | 30.25 | 24.2 | 30.25 | 24.2 | 30.25 | 24.2 | 24.2 | 19.36 | - | - | 35.75 | 28.6 | 35.75 | 28.6 | 37.84 | 30.25 | 37.84 | 30.25 | 38.5 | 30.8
DG184G | 34.43 | 27.5 | 34.43 | 27.5 | 34.43 | 27.5 | 27.5 | 22 | - | - | 41.25 | 33 | 38.5 | 30.8 | 41.25 | 33 | 41.25 | 33 | 41.25 | 33
DG184H | 41.25 | 33 | 41.25 | 33 | 41.25 | 33 | 33 | 26.4 | - | - | 47.85 | 38.28 | 48.73 | 38.94 | 51.59 | 41.25 | 51.59 | 41.25 | 51.59 | 41.25
DG184J | 44 | 35.2 | 44 | 35.2 | 44 | 35.2 | 35.2 | 28.16 | - | - | 52.25 | 41.8 | 52.03 | 41.624 | 55 | 44 | 55 | 44 | 55 | 44
DG224C | 46.75 | 37.4 | 46.75 | 37.4 | 46.75 | 37.4 | 33 | 26.4 | - | - | 60.5 | 48.4 | 55 | 44 | 57.75 | 46.2 | 57.75 | 46.2 | 60.5 | 48.4
DG224D | 55 | 44 | 55 | 44 | 55 | 44 | 41.25 | 33 | - | - | 68.75 | 55 | 66 | 52.8 | 68.75 | 55 | 68.75 | 55 | 71.5 | 57.2
DG224E | 66 | 52.8 | 66 | 52.8 | 66 | 52.8 | 49.5 | 39.6 | - | - | 77 | 61.6 | 74.25 | 59.4 | 77 | 61.6 | 77 | 61.6 | 82.5 | 66
DG224F | 79.75 | 63.8 | 79.75 | 63.8 | 79.75 | 63.8 | 60.5 | 48.4 | - | - | 93.5 | 74.8 | 92.18 | 73.7 | 96.25 | 77 | 96.25 | 77 | 103.18 | 82.544
DG224G | 93.5 | 74.8 | 93.5 | 74.8 | 93.5 | 74.8 | 82.5 | 66 | - | - | 110 | 88 | 103.18 | 82.5 | 107.25 | 85.8 | 110 | 88 | 114.18 | 91.344
DG274C | 110 | 88 | 110 | 88 | 110 | 88 |  |  | - | - | 132 | 105.6 | 123.75 | 99 | 129.25 | 103.4 | 129.25 | 103.4 | 137.5 | 110
DG274D | 137.5 | 110 | 137.5 | 110 | 137.5 | 110 |  |  | - | - | 154 | 123.2 | 154 | 123.2 | 165 | 132 | 165 | 132 | 165 | 132
DG274E | 154 | 123.2 | 154 | 123.2 | 154 | 123.2 |  |  | - | - | 176 | 140.8 | 176 | 140.8 | 184.8 | 147.4 | 184.8 | 147.4 | 195.8 | 156.64
DG274EL | 165 | 132 | 165 | 132 | 165 | 132 |  |  | - | - | 187 | 149.6 | 187 | 149.6 | 198 | 158.4 | 198 | 158.4 | 209 | 167.2
DG274F | 176 | 140.8 | 176 | 140.8 | 176 | 140.8 |  |  | - | - | 198 | 158.4 | 199.1 | 159.28 | 209 | 167.2 | 209 | 167.2 | 220 | 176
DG274G | 198 | 158.4 | 198 | 158.4 | 198 | 158.4 |  |  | - | - | 220 | 176 | 220 | 176 | 234.3 | 187.44 | 234.3 | 187.44 | 242 | 193.6
DG274H | 220 | 176 | 220 | 176 | 220 | 176 |  |  | - | - | 261.25 | 209 | 260.7 | 208.56 | 269.5 | 215.6 | 269.5 | 215.6 | 275 | 220
DG274J | 247.5 | 198 | 247.5 | 198 | 247.5 | 198 |  |  | - | - | 308 | 247.5 | 295.9 | 236.72 | 309.1 | 247.5 | 309.1 | 247.28 | 330 | 264
DG274K | 275 | 220 | 275 | 220 | 275 | 220 |  |  | - | - | 330 | 264 | 320.1 | 256.08 | 330 | 264 | 330 | 264 | 343.75 | 275
DG444C | 275 | 220 | 275 | 220 | 275 | 220 | 275 | 220 | 330 | 264 | 330 | 264 | 316.25 | 253 | 330 | 264 | 330 | 264 | 343.75 | 275
DG444D | 330 | 264 | 330 | 264 | 330 | 264 | 308 | 246.4 | 385 | 308 | 385 | 308 | 374 | 299.2 | 396 | 316.8 | 396 | 316.8 | 412.5 | 330
DGK444D | 344.3 | 275 | 344.3 | 275 | 344.3 | 275 | 319 | 255.2 | 396 | 316.8 | 396 | 316.8 | 385 | 308 | 412.5 | 330 | 412.5 | 330 | 426.8 | 341.44
DG444E | 357.5 | 286 | 357.5 | 286 | 357.5 | 286 | 357.5 | 286 | - | - | - | - | 419.1 | 335.28 | 440 | 352 | 440 | 352 | 456.5 | 365.2
DGK444E | 385 | 308 | 385 | 308 | 385 | 308 | 385 | 308 | - | - | - | - | 440 | 352 | 462 | 369.6 | 462 | 369.6 | 473 | 378.4
DG444F | 412.5 | 330 | 412.5 | 330 | 412.5 | 330 | 412.5 | 330 | 522.5 | 418 | - | - | 488.4 | 390.72 | 500.5 | 400.4 | 509.3 | 407.44 | 522.5 | 418
DGK444F | 440 | 352 | 440 | 352 | 440 | 352 | 440 | 352 | 550 | 440 | - | - | 499.4 | 399.52 | 528 | 422.4 | 550 | 440 | 550 | 440
DG544C | 495 | 396 | 495 | 396 | 495 | 396 | 495 | 396 | 550 | 440 | 550 | 440 | 577.5 | 462 | 605 | 484 | 639.1 | 511.28 | 653.4 | 522.72
DG544D | 550 | 440 | 550 | 440 | 550 | 440 | 550 | 440 | 687.5 | 550 | 687.5 | 550 | 632.5 | 506 | 653.4 | 522.72 | 687.5 | 550 | 708.4 | 566.72
DG544ES | 619.3 | 495.44 | 619.3 | 495 | 619.3 | 495 | 619.3 | 495.44 | 715 | 572 | 715 | 572 | 687.5 | 550 | 715 | 572 | 737 | 589.6 | 770 | 616
DG544E | 660 | 528 | 660 | 528 | 660 | 528 | 660 | 528 | 756.25 | 605 | 756.8 | 605.44 | 749.1 | 599.28 | 784.3 | 627.44 | 805.2 | 644.16 | 825 | 660
DG544EL | 687.5 | 550 | 687.5 | 550 | 687.5 | 550 | 687.5 | 550 | 781 | 624.8 | 781 | 624.8 | 770 | 616 | 808.5 | 646.8 | 830.5 | 664.4 | 841.5 | 673.2
DG544F | 737 | 589.6 | 737 | 589.6 | 737 | 589.6 | 715 | 572 | 880 | 704 | 880 | 704 | 811.8 | 649.44 | 852.5 | 682 | 880 | 704 | 907.5 | 726
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 380-416 |  |  |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 220-240 |  |  |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | - |  | 380-416 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | - |  | 190-208 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | - |  | 220-240 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 13 |  | 14 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DG634B | 781 | 624.8 | 825 | 660 | 825 | 660 | 748 | 598.4 | - | - | 1031.8 | 825 | 891 | 712.8 | 940.5 | 752.4 | 984.5 | 787.6 | 1031.8 | 825.44
DG634C1 | 836 | 668.8 | 880 | 704 | 880 | 704 | 797.5 | 638 | - | - | - | - | 951.5 | 761.2 | 1007.6 | 806.08 | 1053.8 | 843.04 | 1100 | 880
DG634D | 951.5 | 761.2 | 1001 | 800.8 | 1001 | 800.8 | 907.5 | 726 | - | - | 1169.3 | 935 | 1084.6 | 867.68 | 1137.4 | 909.92 | 1199 | 959.2 | 1251.8 | 1001.44
DG634E | 1045 | 836 | 1100 | 880 | 1100 | 880 | 1001 | 800.8 | - | - | 1375 | 1100 | 1191.3 | 953.04 | 1259.5 | 1007.6 | 1316.7 | 1053.36 | 1375 | 1100
DG634F | 1199 | 959.2 | 1243 | 994.4 | 1243 | 994.4 | 1127.5 | 902 | - | - | 1452 | 1161.6 | 1324.4 | 1059.52 | 1401.4 | 1121.12 | 1465.2 | 1172.16 | 1529 | 1223.2
DG634G | 1309 | 1047.2 | 1375 | 1100 | 1375 | 1100 | 1248.5 | 998.8 | 1650 | 1320 | - | - | 1441 | 1152.8 | 1524.6 | 1219.68 | 1593.9 | 1275.12 | 1664.3 | 1331.44
DG734B | 1496 | 1196.8 | 1540 | 1232 | 1540 | 1232 | 1512.5 | 1210 | 1716 | 1372.8 | - | - | 1677.5 | 1342 | 1787.5 | 1430 | 1820.5 | 1456.4 | 1859 | 1487.2
DG734C | 1655.5 | 1324.4 | 1705 | 1364 | 1705 | 1364 | 1672 | 1337.6 | 1947 | 1557.6 | - | - | 1875.5 | 1500.4 | 1996.5 | 1597.2 | 2040.5 | 1632.4 | 2079 | 1663.2
DG734D | 1776.5 | 1421.2 | 1815 | 1452 | 1815 | 1452 | 1782 | 1425.6 | 2106.5 | 1685.2 | - | - | 1996.5 | 1597.2 | 2128.5 | 1702.8 | 2172.5 | 1738 | 2216.5 | 1773.2
DG734E | 2029.5 | 1623.6 | 2090 | 1672 | 2090 | 1672 | 2051.5 | 1641.2 | - | - | - | - | 2277 | 1821.6 | 2431 | 1944.8 | 2475 | 1980 | 2530 | 2024
DG734F | 2222 | 1777.6 | 2288 | 1830.4 | 2288 | 1830.4 | 2244 | 1795.2 | 2750 | 2200 | - | - | 2579.5 | 2063.6 | 2750 | 2200 | 2805 | 2244 | 2860 | 2288
DG734G | 2348.5 | 1878.8 | 2420 | 1936 | 2420 | 1936 | 2376 | 1900.8 | - | - | - | - | 2662 | 2129.6 | 2788.5 | 2230.8 | 2887.5 | 2310 | 3025 | 2420
DG734H | 2497 | 1997.6 | 2574 | 2059.2 | 2574 | 2059.2 | 2530 | 2024 | - | - | - | - | 2777.5 | 2222 | 2904 | 2323.2 | 2997.5 | 2398 | 3113 | 2490.4
Notes：
1. DG634C has no W11 option
2. DGK-foluted fan
3. The above rating is based on one hour rating with no temperature rising list and below 1000 meters altitude above sea.
4. DG734B～H has only W12 option

## Marine 70K
Dingol Marine Generator Rating Table (4-pole,H class insulation,B class temperature rising)
| Environment Temperature: |  |  |  |  | 50 Degree C |  |  | 70K temperature Rising
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DGM184E | 13.3 | 10.64 | 13.3 | 10.64 | 13.3 | 10.64 | - | - | 16 | 22 | 17 | 23 | 17 | 13.6 | 17 | 13.6
DGM184F | 17.5 | 14 | 17.5 | 14 | 17.5 | 14 | - | - | 20.3 | 26 | 21.5 | 27.5 | 21.5 | 17.2 | 21.5 | 17.2
DGM184G | 19.8 | 15.84 | 19.8 | 15.84 | 19.8 | 15.84 | - | - | 23.1 | 18.48 | 24.4 | 19.52 | 24.4 | 19.52 | 24.4 | 19.52
DGM184H | 27 | 21.6 | 27 | 21.6 | 27 | 21.6 | - | - | 31.8 | 25.44 | 33.5 | 26.8 | 33.5 | 26.8 | 33.5 | 26.8
DGM184J | 27.3 | 21.84 | 28.7 | 22.96 | 27.3 | 21.84 | - | - | 32.2 | 25.76 | 34 | 27.2 | 34 | 27.2 | 34 | 27.2
DGM224C | 31 | 24.8 | 31 | 24.8 | 31 | 24.8 | 22.5 | 18 | 35 | 28 | 36.3 | 29.04 | 37.5 | 30 | 37.5 | 30
DGM224D | 37.5 | 30 | 37.5 | 30 | 37.5 | 30 | 27.3 | 21.84 | 42 | 33.6 | 43.8 | 35.04 | 46.3 | 37.04 | 46.3 | 37.04
DGM224E | 42 | 33.6 | 42 | 33.6 | 42 | 33.6 | 32.6 | 26.08 | 47.5 | 38 | 50 | 40 | 52.5 | 42 | 52.5 | 42
DGM224F | 50 | 40 | 50 | 40 | 50 | 40 | 39.3 | 31.44 | 57.5 | 46 | 60 | 48 | 62.5 | 50 | 62.5 | 50
DGM224G | 60 | 48 | 60 | 48 | 60 | 48 | 52.2 | 41.76 | 62.5 | 50 | 68.8 | 55.04 | 75 | 60 | 75 | 60
DGM274C | 67.5 | 54 | 67.5 | 54 | 67.5 | 54 | - | - | 75 | 60 | 77.5 | 62 | 80 | 64 | 80 | 64
DGM274D | 81.3 | 65.04 | 81.3 | 65.04 | 81.3 | 65.04 | - | - | 87.5 | 70 | 90 | 72 | 92.5 | 74 | 92.5 | 74
DGM274E | 100 | 80 | 100 | 80 | 100 | 80 | - | - | 110 | 88 | 112.5 | 90 | 118.8 | 134 | 118.8 | 164.4
DGM274F | 112.5 | 90 | 112.5 | 90 | 112.5 | 90 | - | - | 131.3 | 105.04 | 137.5 | 110 | 143.8 | 115.04 | 143.8 | 115.04
DGM274G | 128.6 | 102.88 | 128.6 | 102.88 | 128.6 | 102.88 | - | - | 151.6 | 121.28 | 162 | 129.6 | 162 | 129.6 | 162 | 129.6
DGM274H | 143.8 | 115.04 | 143.8 | 115.04 | 143.8 | 115.04 | - | - | 175 | 140 | 187.5 | 150 | 200 | 160 | 200 | 160
DGM444C | 175 | 140 | 175 | 140 | 185 | 148 | 185 | 148 | 200 | 160 | 205 | 164 | 220 | 176 | 225 | 180
DGM444D | 195 | 156 | 195 | 156 | 200 | 160 | 200 | 160 | 225 | 180 | 235 | 188 | 248 | 198.4 | 258 | 206.4
DGM444E | 238 | 190.4 | 238 | 190.4 | 240 | 192 | 240 | 192 | 275 | 220 | 285 | 228 | 295 | 236 | 303 | 242.4
DGM444F | 263 | 210.4 | 263 | 210.4 | 273 | 218.4 | 273 | 218.4 | 319 | 255.2 | 330 | 264 | 335 | 268 | 344 | 275.2
DGM544C | 320 | 256 | 325 | 260 | 330 | 264 | 330 | 264 | 375 | 300 | 395 | 316 | 415 | 332 | 420 | 336
DGM544D | 355 | 284 | 365 | 292 | 375 | 300 | 375 | 300 | 405 | 324 | 425 | 340 | 445 | 356 | 465 | 372
DGM544E | 415 | 332 | 430 | 344 | 440 | 352 | 440 | 352 | 495 | 396 | 515 | 412 | 520 | 416 | 530 | 424
DGM544F | 440 | 352 | 460 | 368 | 475 | 380 | 475 | 380 | 544 | 435.2 | 565 | 452 | 578 | 462.4 | 582 | 465.6
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DGM634B | 480 | 384 | 510 | 408 | 510 | 408 | 480 | 384 | 550 | 440 | 580 | 464 | 612 | 489.6 | 625 | 500
DGM634C1 | 515 | 412 | 550 | 440 | 550 | 440 | 510 | 408 | 580 | 464 | 620 | 496 | 650 | 520 | 688 | 550.4
DGM634D | 580 | 464 | 625 | 500 | 625 | 500 | 570 | 456 | 650 | 520 | 700 | 560 | 730 | 584 | 750 | 600
DGM634E | 640 | 512 | 688 | 550.4 | 688 | 550.4 | 630 | 504 | 730 | 584 | 780 | 624 | 815 | 652 | 850 | 680
DGM634F | 730 | 584 | 760 | 608 | 760 | 608 | 720 | 576 | 820 | 656 | 860 | 688 | 900 | 720 | 950 | 760
DGM634G | 812 | 649.6 | 850 | 680 | 850 | 680 | 812 | 649.6 | 880 | 704 | 940 | 752 | 980 | 784 | 1010 | 808
DGM734B | 955 | 764 | 1005 | 804 | 1010 | 808 | 990 | 792 | 1190 | 952 | 1170 | 936 | 1190 | 952 | 1215 | 972
DGM734C | 1080 | 864 | 1115 | 892 | 1115 | 892 | 1095 | 876 | 1225 | 980 | 1305 | 1044 | 1335 | 1068 | 1360 | 1088
DGM734D | 1150 | 920 | 1190 | 952 | 1190 | 952 | 1165 | 932 | 1305 | 1044 | 1390 | 1112 | 1420 | 1136 | 1450 | 1160
DGM734E | 1325 | 1060 | 1370 | 1096 | 1370 | 1096 | 1340 | 1072 | 1490 | 1192 | 1590 | 1272 | 1620 | 1296 | 1655 | 1324
DGM734F | 1450 | 1160 | 1495 | 1196 | 1495 | 1196 | 1460 | 1168 | 1685 | 1348 | 1795 | 1436 | 1835 | 1468 | 1870 | 1496
DGM734G | 1535 | 1228 | 1585 | 1268 | 1585 | 1268 | 1550 | 1240 | 1780 | 1424 | 1900 | 1520 | 1940 | 1552 | 1980 | 1584
DGM734H | 1585 | 1268 | 1635 | 1308 | 1635 | 1308 | 1600 | 1280 | 1840 | 1472 | 1960 | 1568 | 2000 | 1600 | 2040 | 1632
Notes：
1. Environment Protection：IP23
2. With PMG+MX341 AVR
3. With Anti-condensation heater
4. Marine Spec Impregnation
5. The above rating is based on 50 degree C ambient and 70K temperature rising below 1000 meters altitude above sea.
6. DGM634C has no W11 option
7. DGM734B～H has only W12 option
8. For DGM18, the winding is W71 (auxiliary winding + AS440,instead of PMG+MX341)

## Marine - 90K
Dingol Marine Generator Rating Table (4-pole,H class insulation,F class temperature rising)
| Environment Temperature: |  |  |  |  | 50 Degree C |  |  | 90K temperature Rising
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DGM184E | 15 | 12 | 15 | 12 | 15 | 12 | - | - | 18.3 | 14.64 | 19.3 | 15.44 | 19.3 | 15.44 | 19.3 | 15.44
DGM184F | 20 | 16 | 20 | 16 | 20 | 16 | - | - | 23.1 | 18.48 | 24.5 | 19.6 | 24.5 | 19.6 | 24.5 | 19.6
DGM184G | 22.5 | 18 | 22.5 | 25 | 22.5 | 25 | - | - | 26.3 | 21.04 | 27.8 | 22.24 | 27.8 | 22.24 | 27.8 | 22.24
DGM184H | 30.6 | 24.48 | 30.6 | 24.48 | 30.6 | 24.48 | - | - | 35.9 | 28.72 | 37.8 | 30.24 | 37.2 | 29.76 | 37.8 | 30.24
DGM184J | 30.9 | 24.72 | 32.6 | 26.08 | 30.9 | 24.72 | - | - | 36.5 | 29.2 | 38.7 | 30.96 | 38.7 | 30.96 | 38.7 | 30.96
DGM224C | 35 | 28 | 35 | 28 | 35 | 28 | 25.5 | 20.4 | 39.4 | 31.52 | 41.9 | 33.52 | 43.1 | 34.48 | 43.1 | 34.48
DGM224D | 40 | 32 | 40 | 32 | 40 | 32 | 29.7 | 23.76 | 47.5 | 38 | 50 | 40 | 51.3 | 41.04 | 51.3 | 41.04
DGM224E | 47.5 | 38 | 47.5 | 38 | 47.5 | 38 | 36.9 | 29.52 | 53.8 | 43.04 | 56.3 | 45.04 | 58.8 | 47.04 | 58.8 | 47.04
DGM224F | 57.5 | 46 | 57.5 | 46 | 57.5 | 46 | 45.2 | 36.16 | 65.6 | 52.48 | 68.8 | 55.04 | 71.9 | 57.52 | 71.9 | 57.52
DGM224G | 65 | 52 | 65 | 52 | 65 | 52 | 52.2 | 41.76 | 75 | 60 | 78.8 | 63.04 | 81.3 | 65.04 | 81.3 | 65.04
DGM274C | 77.5 | 62 | 100 | 80 | 100 | 80 | - | - | 90 | 72 | 92.5 | 74 | 97.5 | 78 | 97.5 | 78
DGM274D | 87.5 | 70 | 125 | 100 | 125 | 100 | - | - | 107.5 | 86 | 110 | 88 | 112.5 | 90 | 112.5 | 90
DGM274E | 112.5 | 90 | 140 | 112 | 140 | 112 | - | - | 125 | 100 | 131.3 | 105.04 | 137.5 | 134 | 130.5 | 127
DGM274F | 135 | 108 | 160 | 128 | 160 | 128 | - | - | 150 | 120 | 156 | 124.8 | 163.5 | 130.8 | 163.5 | 130.8
DGM274G | 149 | 119.2 | 180 | 144 | 180 | 144 | - | - | 170.7 | 136.56 | 186 | 148.8 | 186.5 | 149.2 | 186.5 | 149.2
DGM274H | 170 | 136 | 200 | 160 | 200 | 160 | - | - | 200 | 160 | 212.5 | 170 | 218.8 | 175.04 | 218.8 | 175.04
DGM444C | 210 | 168 | 210 | 168 | 210 | 168 | 210 | 168 | 240 | 192 | 245 | 196 | 250 | 200 | 255 | 204
DGM444D | 230 | 184 | 230 | 184 | 230 | 184 | 230 | 184 | 255 | 204 | 270 | 216 | 280 | 224 | 295 | 236
DGM444E | 275 | 220 | 275 | 220 | 275 | 220 | 275 | 220 | 315 | 252 | 325 | 260 | 340 | 272 | 345 | 276
DGM444F | 310 | 248 | 310 | 248 | 310 | 248 | 310 | 248 | 365 | 292 | 375 | 300 | 380 | 304 | 395 | 316
DGM544C | 365 | 292 | 370 | 296 | 380 | 304 | 380 | 304 | 431 | 344.8 | 450 | 360 | 475 | 380 | 481 | 384.8
DGM544D | 405 | 324 | 415 | 332 | 430 | 344 | 430 | 344 | 463 | 370.4 | 488 | 390.4 | 506 | 404.8 | 531 | 424.8
DGM544E | 475 | 380 | 490 | 392 | 505 | 404 | 505 | 404 | 563 | 450.4 | 588 | 470.4 | 594 | 475.2 | 606 | 484.8
DGM544F | 505 | 404 | 525 | 420 | 540 | 432 | 540 | 432 | 619 | 495.2 | 644 | 515.2 | 656 | 524.8 | 663 | 530.4
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DGM634B | 550 | 440 | 583 | 466.4 | 583 | 466.4 | 550 | 440 | 630 | 504 | 665 | 532 | 696 | 556.8 | 730 | 584
DGM634C1 | 592 | 473.6 | 625 | 500 | 625 | 500 | 580 | 464 | 670 | 536 | 713 | 570.4 | 745 | 596 | 778 | 622.4
DGM634D | 673 | 538.4 | 708 | 566.4 | 708 | 566.4 | 650 | 520 | 767 | 613.6 | 811 | 648.8 | 848 | 678.4 | 886 | 708.8
DGM634E | 739 | 591.2 | 778 | 622.4 | 778 | 622.4 | 720 | 576 | 840 | 672 | 891 | 712.8 | 931 | 744.8 | 972 | 777.6
DGM634F | 848 | 678.4 | 879 | 703.2 | 879 | 703.2 | 820 | 656 | 936 | 748.8 | 990 | 792 | 1035 | 828 | 1081 | 864.8
DGM634G | 925 | 740 | 972 | 777.6 | 972 | 777.6 | 880 | 704 | 1018 | 814.4 | 1077 | 861.6 | 1126 | 900.8 | 1175 | 940
DGM734B | 1033.6 | 826.88 | 1064 | 851.2 | 1064 | 851.2 | 1045 | 836 | 1159 | 927.2 | 1235 | 988 | 1257.8 | 1006.24 | 1284.4 | 1027.52
DGM734C | 1180 | 944 | 1240 | 992 | 1240 | 992 | 1125 | 900 | 1390 | 1112 | 1480 | 1184 | 1510 | 1208 | 1540 | 1232
DGM734D | 1255 | 1004 | 1320 | 1056 | 1320 | 1056 | 1200 | 960 | 1480 | 1184 | 1580 | 1264 | 1610 | 1288 | 1645 | 1316
DGM734E | 1365 | 1092 | 1435 | 1148 | 1435 | 1148 | 1300 | 1040 | 1690 | 1352 | 1800 | 1440 | 1840 | 1472 | 1875 | 1500
DGM734F | 1500 | 1200 | 1580 | 1264 | 1580 | 1264 | 1450 | 1160 | 1910 | 1528 | 2035 | 1628 | 2075 | 1660 | 2120 | 1696
DGM734G | 1740 | 1392 | 1795 | 1436 | 1795 | 1436 | 1700 | 1360 | 2020 | 1616 | 2155 | 1724 | 2200 | 1760 | 2245 | 1796
DGM734H | 1790 | 1432 | 1845 | 1476 | 1845 | 1476 | 1750 | 1400 | 2080 | 1664 | 2215 | 1772 | 2260 | 1808 | 2305 | 1844
Notes：
1. Environment Protection：IP23
2. With PMG+MX341 AVR
3. With Anti-condensation heater
4. Marine Spec Impregnation
5. The above rating is based on 50 degree C ambient and 90K temperature rising below 1000 meters altitude above sea.
6. DGM634C has no W11 option
7. DGM734B～H has only W12 option
8. For DGM18, the winding is W71 (auxiliary winding + AS440,instead of PMG+MX341)

## Marine 110K
Dingol Marine Generator Rating Table (4-pole,H class insulation,H class temperature rising)
| Environment Temperature: |  |  |  |  | 50 Degree C |  |  | 110K temperature Rising
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Parallel delta | 110 |  | 115 |  | 120 |  | 127 |  | 120 |  | 127 |  | 133 |  | 138.5
Winding No. | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DGM184E | 16.5 | 13.2 | 16.5 | 13.2 | 16.5 | 13.2 | - | - | 20 | 16 | 21.3 | 17.04 | 21.3 | 17.04 | 21.3 | 17.04
DGM184F | 22 | 17.6 | 22 | 17.6 | 22 | 17.6 | - | - | 25.4 | 20.32 | 27 | 21.6 | 27 | 21.6 | 27 | 21.6
DGM184G | 24.8 | 25 | 25.2 | 25.4 | 25.6 | 25.8 | - | - | 27.9 | 22.32 | 29.5 | 23.6 | 29.5 | 23.6 | 29.5 | 23.6
DGM184H | 33.8 | 27.04 | 33.8 | 27.04 | 33.8 | 27.04 | - | - | 39.9 | 31.92 | 42 | 33.6 | 42 | 33.6 | 42 | 33.6
DGM184J | 34.2 | 27.36 | 34.2 | 27.36 | 34.2 | 27.36 | - | - | 40.4 | 32.32 | 42.8 | 34.24 | 42.8 | 34.24 | 42.8 | 34.24
DGM224C | 38 | 30.4 | 38 | 30.4 | 38 | 30.4 | 26.8 | 21.44 | 43.8 | 35.04 | 44.7 | 35.76 | 44.7 | 35.76 | 46.5 | 37.2
DGM224D | 44 | 35.2 | 44 | 35.2 | 44 | 35.2 | 32.7 | 26.16 | 51 | 40.8 | 52.1 | 41.68 | 54.3 | 43.44 | 56.3 | 45.04
DGM224E | 52.3 | 41.84 | 52.3 | 41.84 | 52.3 | 41.84 | 40.2 | 32.16 | 60 | 48 | 63 | 50.4 | 63 | 50.4 | 66 | 52.8
DGM224F | 63.3 | 50.64 | 63.3 | 50.64 | 63.3 | 50.64 | 49.1 | 39.28 | 72.5 | 58 | 75.6 | 60.48 | 75.6 | 60.48 | 80 | 64
DGM224G | 71.5 | 57.2 | 71.5 | 57.2 | 71.5 | 57.2 | 62.7 | 50.16 | 84.5 | 67.6 | 87 | 69.6 | 91 | 72.8 | 92 | 73.6
DGM274C | 81.5 | 65.2 | 81.5 | 65.2 | 81.5 | 65.2 | - | - | 93.8 | 75.04 | 102.5 | 82 | 102.5 | 82 | 108.8 | 87.04
DGM274D | 97 | 77.6 | 97 | 77.6 | 97 | 77.6 | - | - | 115 | 92 | 117.5 | 94 | 120 | 96 | 125 | 100
DGM274E | 120 | 96 | 120 | 96 | 120 | 96 | - | - | 135 | 108 | 137.5 | 110 | 140 | 134 | 144 | 127
DGM274F | 140 | 112 | 140 | 112 | 140 | 112 | - | - | 156.3 | 125.04 | 162.5 | 130 | 167.5 | 134 | 168.8 | 135.04
DGM274G | 159 | 127.2 | 159 | 127.2 | 159 | 127.2 | - | - | 186.4 | 149.12 | 192.8 | 154.24 | 192.8 | 154.24 | 205.7 | 164.56
DGM274H | 175 | 140 | 175 | 140 | 175 | 140 | - | - | 212.5 | 170 | 218.8 | 175.04 | 221.3 | 177.04 | 225 | 180
DGM444C | 210 | 168 | 210 | 168 | 215 | 172 | 215 | 172 | 256 | 204.8 | 262 | 209.6 | 265 | 212 | 269 | 215.2
DGM444D | 235 | 188 | 235 | 188 | 240 | 192 | 240 | 192 | 295 | 236 | 305 | 244 | 320 | 256 | 330 | 264
DGM444E | 290 | 232 | 290 | 232 | 295 | 236 | 295 | 236 | 337 | 269.6 | 350 | 280 | 362 | 289.6 | 370 | 296
DGM444F | 330 | 264 | 330 | 264 | 340 | 272 | 340 | 272 | 394 | 315.2 | 406 | 324.8 | 413 | 330.4 | 425 | 340
DGM544C | 390 | 312 | 390 | 312 | 390 | 312 | 390 | 312 | 463 | 370.4 | 485 | 388 | 515 | 412 | 520 | 416
DGM544D | 435 | 348 | 435 | 348 | 435 | 348 | 435 | 348 | 500 | 400 | 520 | 416 | 545 | 436 | 570 | 456
DGM544E | 530 | 424 | 530 | 424 | 530 | 424 | 530 | 424 | 606 | 484.8 | 625 | 500 | 638 | 510.4 | 650 | 520
DGM544F | 565 | 452 | 585 | 468 | 600 | 480 | 600 | 480 | 663 | 530.4 | 694 | 555.2 | 706 | 564.8 | 725 | 580
Model | Three Phase 50Hz 1500RPM | [7 empty] | Three Phase 60Hz 1800RPM
Power Factor | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
Volts
Star(W12&W13) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Delta(W12&W13) | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Series Star(W11&W14) | 380 |  | 400 |  | 415 |  | 440 |  | 416 |  | 440 |  | 460 |  | 480
Parallel Star(W11&W14) | 190 |  | 200 |  | 208 |  | 220 |  | 208 |  | 220 |  | 230 |  | 240
Series Delta | 220 |  | 230 |  | 240 |  | 254 |  | 240 |  | 254 |  | 266 |  | 277
Winding No. | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12 |  | 11/12
Rating | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW | KVA | KW
DGM634B | 580 | 464 | 625 | 500 | 625 | 500 | 580 | 464 | 680 | 544 | 710 | 568 | 730 | 584 | 750 | 600
DGM634C1 | 630 | 504 | 687 | 549.6 | 687 | 549.6 | 630 | 504 | 710 | 568 | 750 | 600 | 780 | 624 | 800 | 640
DGM634D | 700 | 560 | 750 | 600 | 750 | 600 | 700 | 560 | 800 | 640 | 850 | 680 | 870 | 696 | 900 | 720
DGM634E | 750 | 600 | 825 | 660 | 825 | 660 | 750 | 600 | 880 | 704 | 930 | 744 | 970 | 776 | 1000 | 800
DGM634F | 850 | 680 | 900 | 720 | 900 | 720 | 850 | 680 | 960 | 768 | 1010 | 808 | 1065 | 852 | 1125 | 900
DGM634G | 950 | 760 | 1030 | 824 | 1030 | 824 | 950 | 760 | 1040 | 832 | 1100 | 880 | 1150 | 920 | 1230 | 984
DGM734B | 1095.616 | 876.4928 | 1127.84 | 902.272 | 1127.84 | 902.272 | 1107.7 | 886.16 | 1228.54 | 982.832 | 1309.1 | 1047.28 | 1333.268 | 1066.6144 | 1361.464 | 1089.1712
DGM734C | 1250.8 | 1000.64 | 1314.4 | 1051.52 | 1314.4 | 1051.52 | 1192.5 | 954 | 1473.4 | 1178.72 | 1568.8 | 1255.04 | 1600.6 | 1280.48 | 1632.4 | 1305.92
DGM734D | 1330.3 | 1064.24 | 1399.2 | 1119.36 | 1399.2 | 1119.36 | 1272 | 1017.6 | 1568.8 | 1255.04 | 1674.8 | 1339.84 | 1706.6 | 1365.28 | 1743.7 | 1394.96
DGM734E | 1446.9 | 1157.52 | 1521.1 | 1216.88 | 1521.1 | 1216.88 | 1378 | 1102.4 | 1791.4 | 1433.12 | 1908 | 1526.4 | 1950.4 | 1560.32 | 1987.5 | 1590
DGM734F | 1590 | 1272 | 1674.8 | 1339.84 | 1674.8 | 1339.84 | 1537 | 1229.6 | 2024.6 | 1619.68 | 2157.1 | 1725.68 | 2199.5 | 1759.6 | 2247.2 | 1797.76
DGM734G | 1844.4 | 1475.52 | 1902.7 | 1522.16 | 1902.7 | 1522.16 | 1802 | 1441.6 | 2141.2 | 1712.96 | 2284.3 | 1827.44 | 2332 | 1865.6 | 2379.7 | 1903.76
DGM734H | 1897.4 | 1517.92 | 1955.7 | 1564.56 | 1955.7 | 1564.56 | 1855 | 1484 | 2204.8 | 1763.84 | 2347.9 | 1878.32 | 2395.6 | 1916.48 | 2443.3 | 1954.64
Notes：
1. Environment Protection：IP23
2. With PMG+MX341 AVR
3. With Anti-condensation heater
4. Marine Spec Impregnation
5. The above rating is based on 50 degree C ambient and 110K temperature rising below 1000 meters altitude above sea.
6. DGM634C has no W11 option
7. DGM734B～H has only W12 option
8. For DGM18, the winding is W71 (auxiliary winding + AS440,instead of PMG+MX341)